## Slide 1: 37th Annual State Construction Conference
Mechanical Code 2018 Updates and Highlights
Tom Galdi, PE
3/29/2018
Notes: I’m going to talk about mechanical code changes – and after that will talk about energy code changes. It’s been six years since we’ve had a code update so the new NC Code will incorporate two iterations of change from the international base codes. There are a lot of changes of varying significance – so this is not a comprehensive update document that covers everything, rather it touches on topics that are fairly common to projects we review, topics that may be poorly understood, or even controversial – we’re not gonna hide from it were gonna take it on.

## Slide 2
NC Amendments
2018
NCMC
Coming 7/1/18
Reqd 1/1/19
Notes: The code is based on the 2015 IMC. The ad-hoc committee administered by DOI reviews the 2015 IMC and adds and deletes material they feel is in the interest of the State and it becomes the 2018 NCMC.

## Slide 3: Alternate Materials and Methods
105.2 The provisions of this code are not intended to prevent the installation of any material or to prohibit any method of construction not specifically prescribed by this code, provided that any such alternative has been approved. An alternative material or method of construction shall be approved where the code official finds that the proposed design is satisfactory and complies with the intent of the provisions of this code, and that the material, method or work offered is, for the purpose intended, not less than the equivalent of that prescribed in this code in quality, strength, effectiveness, fire resistance, durability and safety. Where the alternative material, design or method of construction is not approved, the code official shall respond in writing, stating the reasons the alternative was not approved.
New

## Slide 4: Condensate Drainage
307.4.2.1 Ductless mini-split equipment that produces condensate shall be provided with an inline check valve located in the drain line, or a trap.
Waterless Trap
New
This will also apply to VRF systems
Notes: Starting in 3 and working up : ----
The code has always said and still says - traps are per manufacturer instructions.
Manuf Inst wont call for a trap on these as the condensate pan is not subject to static pressure of the fan.
This is an added requirement to keep out insects or moisture from accessing this pathway..
Does it apply to VRF systems? Yes.

## Slide 5: Condensate Discharge
Include Means to Clean out condensate piping without cutting pipe.
New
Notes: These things often come with an internal condensate pump and can be connected to for gravity draining or pumped draining.
The thing is, these units and trap or check valve devices always seem to come with connections for 5/8” OD vinyl tubing. So one might wonder how this works with the ¾” ID condensate piping requirement that is standard code.
It’s a good question.
I see it as you pump through the tubing up to your allowable height for the pump and then once you start your gravity drain you transition to ¾”. For the graivity drain, I think you can use the tubing at the unit and trap and then transition.

## Slide 6: CARBON MONOXIDE DETECTORS
313 Where required. Carbon monoxide detection shall be provided in Group I-1, I-2, I-4 and R occupancies (Except R-3)
Combination CO and Smoke alarms listed per UL 2034 and UL 217
Notes: CO Alarm requirements were added during the last code cycle and now theres an extensive section in the book; underlined as it is a NC requirement.
It applies I and R occupancies where people are sleeping

## Slide 7: CARBON MONOXIDE DETECTION
Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms if carbon monoxide detection is provided in one of the following locations:
  In an approved location between the fuel-burning appliance or fuel-burning fireplace and the dwelling unit, sleeping unit or classroom.
  On the ceiling of the room containing the fuel-burning appliance or fuel-burning fireplace.
Maintain in accordance with NFPA 720
Notes: The bottom line is if you have fuel fired equipment in a mechanical room you only need a detector in that mechanical room. Language about putting one in every sleeping quarters on that level and the level above is still there but is intended for within a dwelling unit.
Note that unlike the CO detector that was installed in your house, this requirement references NFPA 420. It is to be tested at initial inspection, with CO, introduced to the sensing port; and inspected annually.

## Slide 8
CO Detector at Fireplace
CO Detector at Water Htr
CO Detector at Gas Range

## Slide 9: New in Commercial Kitchens
New: Include air balance schedule or diagram

## Slide 10: Grease Reservoirs
506.3.7.1 Grease duct reservoirs. Grease duct reservoirs shall:
Be constructed as required for the grease duct they serve.
Be located on the bottom of the horizontal duct or the bottommost section of the duct riser.
Extend across the full width of the duct and have a length of not less than 12 inches (305 mm).
Have a depth of not less than 1 inch (25 mm).
Have a bottom that slopes to a drain.
Be provided with a cleanout opening constructed in accordance with Section 506.3.8 and installed to provide direct access to the reservoir. The cleanout opening shall be located on a side or on top of the duct so as to permit cleaning of the reservoir.
Be installed in accordance with the manufacturer’s instructions where manufactured devices are utilized.
New
Notes: All Kitchen grease duct is required to slope toward the hood or toward a reservoir. Specific requirements for a reservoir have been added.
A lot of times I think we manage to avoid a reservoir but there is also a section added on underground grease duct which mandates reservoirs at each end of the underground run.

## Slide 11: Commercial Kitchens
Downdraft exhaust table
507.2 Type I Hoods
Exception: A Type I hood shall not be required for an electric cooking appliance where an approved testing agency provides documentation that the appliance effluent contains 5 mg/m3 or less of grease when tested at an exhaust flow rate of 500 cfm (0.236 m3/s) in accordance with UL 710B.
New
Notes: I saw this section about Type I hoods not being required for equipment that meets this effluent standard and thought maybe this was solving the conundrum of when to use a Type I hood.
But no, you wont find standard cooking equipment tested to this. This is for recirculation hoods or as shown here, a downdraft table.
So as we see, there is an expanding recognition of a trend toward more island type of cooking applications.

## Slide 12: Type 1 Hood Question
Conveyor Style Oven – Yes Type 1 Hood
Deck Style –No Type 1 hood
Still a Judgment Call
Type 2 Hood – If No Type 2 hood
Exhaust space per Chpt 4
Notes: So, To Type I or not is still a judgement call and will still vary among jurisdictions.
Pizza ovens seem to be a common item that falls in the gray area.
One possible view on this would be that conveyer type ovens would be more likely to involve grease and smoke and would require a Type I hood whereas a deck type oven maybe not so much.

## Slide 13: 505 Domestic Cooking Appliances
505.1 Dwelling Unit
R-2 Common Area
505.4 Other Occupancy
25 CFM Exhaust
I-1 and I-2
Hood must exhaust
Fire Suppression Standard Practice.
(not code)
Ventilate spaces per Chpt 4. If Kitchen, exhaust required

## Slide 14: Hazardous Exhausts
510.5 Incompatible materials and common shafts. Incompatible materials, as defined in the International Fire Code, shall not be exhausted through the same hazardous exhaust system. Hazardous exhaust systems shall not share common shafts with other duct systems, except where such systems are hazardous exhaust systems originating in the same fire area.
Ever Changing Interpretations
Notes: Hazardous exhausts is a section that can be and has been interpreted many different ways.
It’s hard to understand and I’ve never seen or heard an explanation of it that fully made sense.
What we mostly deal with are educational and research labs. When you got that, you deal with the list of exceptions; this business here about not sharing shafts you can ignore altogether.

## Slide 15: Exception for Labs Where All These Apply
All of the hazardous exhaust ductwork and other laboratory exhaust within both the occupied space and the shafts are under negative pressure while in operation.
The hazardous exhaust ductwork manifolded together within the occupied space must originate within the same fire area.
Hazardous exhaust ductwork originating in different fire areas and manifolded together in a common shaft shall meet the provisions of Section 717.5.3, Exception 1, Item 1.1 of the International Building Code.
Each control branch has a flow regulating device.
Perchloric acid hoods and connected exhaust shall be prohibited from manifolding.
Radioisotope hoods are equipped with filtration, carbon beds or both where required by the registered design professional.
Biological safety cabinets are filtered.
Each hazardous exhaust duct system shall be served by redundant exhaust fans that comply with either of the following:
  The fans shall operate simultaneously in parallel and each fan is capable of entire exhaust rate.
  Each redundant fan controlled to operate when other fan is failed or shut down for service.
New
New
Notes: So were into the exceptions for labs. You must comply with them all,
They’ve added this one.
So strictly speaking, the apparent interpretation was that you couldn’t combine exhausts from different fire areas.
What’s a fire area? Any area bounded by fire ratings so if you have a room that is rated for whatever reason, that’s a fire area. Most common in the labs is a rated floor. So the issue becomes manifolding exhausts from different floors.
The new add addresses this head on and says you can do it if you comply with that section which talks about 22” subducts.

## Slide 16: Separate Exhaust per Fire Area
Notes: So how we were supposed to be exhausting fume hoods from different floors might have looked something like this.
Separate exhausts and either combined on the roof or more fans on the roof.

## Slide 17: Manifolding Lab Exhausts with Sub Ducts
Notes: Here we see lab exhausts and general exhausts all from different floors manifolded together and your N+1 lab exhaust fans on the roof with opportunity for energy recovery.
Note the 22” subducts

## Slide 18: Sub Ducts
Notes: Shown here as a prefabricated duct
And here as it might be detailed on a plan

## Slide 19: Sub Duct
Notes: And here as it might look in the field.

## Slide 20: 607.5.3 Fire Damper Exceptions in Fire Partitions
Exception: In occupancies other than Group H, fire dampers are not required where any of the following apply:
1. Corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 of the International Building Code and the duct is protected as a through penetration in accordance with Section 714 of the International Building Code.
2. The partitions are tenant partitions in covered and open mall buildings where the walls are not required by provisions elsewhere in the International Building Code to extend to the underside of the floor or roof sheathing, slab or deck above.
4. Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, and are in areas of other than Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 of the International Building Code. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than 26 gage in thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals
New
Notes: Section added which is identical to wording from the fire barrier exemptions.
As it was worded, exemptions 1 and 2 didn’t cover all the fire partitions and there was no reason for that..
For example, a fire partition separating dwelling units.
Ducted with 26 gauge min sheet metal and continuous to the terminal.
Doesn’t mean no flex

## Slide 21: Can This Meet FD Exemption?
Rated Fire Partition
Wall Grill
Notes: Through ducted.

## Slide 22: Duct Penetration Without a Fire Damper
UL Detail Needed
Notes: When we do exempt the FD, need instructions on how to seal the penetration. There is no manufacturer installation instructions as there is with a FD

## Slide 23: Pressurized Elevator and Stair Shafts
Stairwell Pressurization
(high rises)
Hoistway Pressurization (Elevator Lobby alternate)
Notes: When do we have pressurized elevator shafts or Pressurized stairwells.
New Construction. Stair pressurization is allowed instead of a smokeproof enclosure. 0.1” to 0.35 inch of positive pressure with doors closed.

## Slide 24: Smoke Control Requirements Apply
513.6.3 Pressurized stairways and elevator hoistways. Where stairways or elevator hoistways are pressurized, such pressurization systems shall comply with Section 513 as smoke control systems, in addition to the requirements of Sections 909.20 of the International Building Code and 909.21 of the International Fire Code.
These Systems Require Spec. Insp. Etc.
New
Notes: Sometimes in the past these systems might have flown under the radar a little bit but now it’s clear,
they are treated the same as a smoke control system. Analysis, Special inspections, backup power, pressure measurement.

## Slide 25: Duct Detectors
606.4.1 Supervision. The duct smoke detectors shall be connected to a fire alarm system where a fire alarm system is required by Section 907.2 of the International Fire Code. The actuation of a duct smoke detector shall activate a visible and audible supervisory signal at a constantly attended location. In facilities that are required to be monitored by a supervising station, duct smoke detectors shall report only as a supervisory signal, not as a fire alarm.
Duct detectors have specific purpose
New
Notes: Read highlight.
Shall report as a supervisory signal, not as a fire alarm.
Shall means shall; sometimes we think it means at a minimum.
If you want more fire detection, put in more smoke detectors. That’s not what duct detectors are for. Fire alarms from dirty duct detectors in airstreams is not going above and beyond code. It’s a problem.

## Slide 26: 6.7.3.3.2 Smoke Damper Actuation
#5. Where a smoke detection system is installed in all areas served by the duct in which the damper will be located, the smoke dampers shall be permitted to be controlled by the smoke detection system.
5 ways
Words ‘Total Coverage’ have been removed
Notes: There are 5 ways listed for closing smoke dampers.
The last way about using the building general alarm system is by far the easiest provided you have smoke detectors in all areas served by the duct system.
The words total coverage used to be here and those words would scare people off from using this option but the concept really didn’t fit here at all.
Where we run into problems is there is the fire alarm designers wont put smoke detectors in bathrooms with showers because of the steam. So why is it a good idea to put duct detectors in ducts that serve these spaces?
This is the conundrum that continues to be a weakness in the code. It is possible in some applications to use alternate means to allow the general alarm to shut the duct detectors. We have done it in residence halls.

## Slide 27: 1001.1 Boilers, Water Heaters, and Pressure Vessels
1001.1 Scope.
See NCGS Chpt 95, Article 7A, Section 95-69.10 for a complete list of equipment exempt from this code but under jurisdiction of the Dept of Labor.
New
Used to list criteria for DOL jurisdiction, Generally >200,000 btuh or 120 Gal.
Instantaneous Heaters > 400,000 btuh inspected
Notes: This new reference to the GS giving inspection authority to DOL for certain equipment is added.s
Note that vessels heated with steam or electricity over the capacity limit also require DOL certificates but they wouldn’t require the emergency fuel shutoff switch that is at all required egress doors.

## Slide 28
199,000 btuh
119 Gal
No DOL Inspection
Dom. WH > 200,000 btuh
DOL Inspects
No E-stop due to ‘HLW’ stamp
Boiler > 200,000 btuh
DOL Inspects
Has ‘H’ stamp
Yes E-stop (Gas or Electric)
Can shut off control circuit

## Slide 29: Chapter 11 Refrigeration (Chiller Controls)

## Slide 30: Chapter 11 Refrigeration (Chiller Controls)
1106.5 Remote Control of equipment and appliances in machinery room shall comply with 1106.5.1 and 1106.5.2
1106.5.1 Refrigeration system emergency shutoff. A clearly identified switch of the break-glass type or with an approved tamper-resistant cover shall provide off-only control of refrigerant compressors, refrigerant pumps, and normally closed, automatic refrigerant valves located in the machinery room. Additionally, this equipment shall be automatically shut off whenever the refrigerant vapor concentration in the machinery room exceeds the vapor detector’s upper detection limit or 25 percent of the LEL, whichever is lower.
Words Brought Over From Fire Code
Note that 1106 is for higher toxicity or higher flammability refrigerants.
Used to reference fire code
Notes: These are the same words that were in the fire code about emergency shutoff switches.
They’ve been brought to the mechanical code into section 1106 – the special requirements section. In the fire code there wasn’t as clear a delineation for requirments between lower frammability or toxiicity refrigerants versus higher flammability/toxicity refrigerants.
This allowed people to assume requirements meant for the higher hazard chiller rooms were meant for all chiller rooms. They weren’t.
The minimum code shutoff switch requirements for R-134A, R123, R410A – the refrigerants we mostly encounter, is nothing.

## Slide 31: 2015 NC Existing Building Code
Alt’s Level 1
Replace Existing
Maintain Existing Level of Fire Protection
Alt’s Level 2
Level 1 Requirements Plus
5 cfm/person OA and 15 CFM/person total
Alt’s Level 3
Level 1 and 2 Plus
Some reqts on duct detectors and boiler ratings

## Slide 32
Code
Notes: I like trivia so were going to give everyone a chance to win some money. This is multiple choice Jeopardy. Keep your own score. The categories are:

## Slide 33
History
$100
$400
Ducts n Things
$100
$400
In The Kitchen
$100
$400
$200
$200
$200
$300
$300
$300
Chapter 1
Admin
$100
$400
$200
$300

## Slide 34: Ducts n Things
This duct system product does not require UL certification
What is Internal Insulation
What are Diffusers, Registers
What is a Flexible Connector
What is Duct Tape
UL 181
604.13
UL 181
603.6.2
UL 181
603.9
603.18

## Slide 35
History
$100
$400
Ducts n Things
$100
$400
In The Kitchen
$100
$400
$200
$200
$200
$300
$300
$300
Chapter 1
Admin
$100
$400
$200
$300

## Slide 36: Chapter 1 Admin
The NCMC has basic instructions for the installation of an appliance. It also references an applicable NFPA standard. The maximum allowed vent length varies per the source document:
What is the legally required maximum vent length?
Man. Inst. Instructions
30 feet
NC Mechanical Code
20 feet
Ref. NFPA Standard
15 feet
102.8.2 – Code takes precedence over referenced standards
304.2 – Most restrictive between manufacturer and code applies

## Slide 37
History
$100
$400
Ducts n Things
$100
$400
In The Kitchen
$100
$400
$200
$200
$200
$300
$300
$300
Chapter 1
Admin
$100
$400
$200
$300

## Slide 38: In The Kitchen
This is what requires shut down of Makeup air upon Hood Fire Suppression system activation.
What is the Mechanical Code?
What is the Fire Code?
What is NFPA 96?
What is the Equipment Listing?
What is … It’s a mystery?

## Slide 39
History
$100
$400
Ducts n Things
$100
$400
In The Kitchen
$100
$400
$200
$200
$200
$300
$300
$300
Chapter 1
Admin
$100
$400
$200
$300

## Slide 40: History
The International Codes were introduced in this year shortly before being adopted in North Carolina.
What is …
1492
1925
1945
2000

## Slide 41: History
The international codes were introduced in this year shortly before being adopted by North Carolina.
What is …
1492

## Slide 42: History
The International Codes were introduced in this year shortly before being adopted by NC.
What is …
1925

## Slide 43: History
The International Codes were introduced in this year shortly before being adopted by North Carolina.
What is …
1945

## Slide 44: History
The International Codes were introduced in this year shortly before being adopted by North Carolina.
What is …
1492
1925
1977
2000

## Slide 45: 37th ANNUAL State Construction Conference
2018 North Carolina Energy Conservation Code Updates and Highlights
Tom Galdi, PE 3/29/18

## Slide 46
18.2%
2018
NCECC
7.6%
2007
2010
2013
2009
2012
2015
2012
2018
ASHRAE
ICC
NC
Notes: The new NC code is again based on the 2015 International code which again has 2 code cycle updates since our code was last updated. The I codes are very similar to ASHRAE. Estimated % savings are shown here – 2013 has less savings over the previous cycle than 2010 did.
You can see I drew the 2018 code offset a little bit. Though it’s based on ASHRAE 2013 as far as the equipment efficiency tables and insulation requirements, there are enough requirements lined through by the ad hoc committee that it wouldn’t be considered to meet that.
By contrast, our 2012 code actually had some insulation requirements that were beyond 2007 ASHRAE.

## Slide 47: Paths to Compliance
2018 NCECC
2018 NCECC
Notes: 3 main paths to compliance
90.1-2013 – you meet that your beyond our code.
Perscriptive – most common – do what code calls for.
Performance – A total building performance energy model with the proposed building not exceeding 85% of the cost (not energy) of the baseline building. How to establish your baseline is covered right here in the code. It was in there before but kind of un-noticed because the NC changes had replaced this compliance path with one that referenced 90.1 APP G – which might have been short-sighted because App G had never been intended for use as a compliance path - and that path was ultimately deleted in favor of 90.1-2010 compliance.
Anyway, there are mandatory requirements. Perscriptive requirements and envelope requirements are fair game for trading off.
Comcheck is also referenced – we don’t see it used much – it is for envelope trading only. Mechanical is all prescriptive.
If you want to build a building of all glass, there are numerous paths around the prescriptive limits.

## Slide 48
Additional High Efficiency Option Must be Selected
Enhanced Lighting Controls
More Efficient HVAC
DOAS w/ Heat Recovery
Reduced Lighting Power Density
On-Site Renewables
Notes: In our prescriptive path we have to do something special.
These are the choices.

## Slide 49: HVAC Mandatory Requirements
C403.2.4 HVAC System Controls
  Thermostat Deadbands
  Thermostat Setbacks
C403.2.5 Hot Water Boiler Outdoor Temp Setback
C403.2.6.1 Demand Controlled Ventilation – Now all spaces > 500 sq ft and occupancy load of 25 people per 1000 sq ft or greater. Also, any system with OA > 3000 CFM.
Demand Controlled Ventilation is intended to conserve energy by the reduction of ventilation air below design during periods when occupancy is below design.
Notes: In all cases there are mandatory requirements. They may vary a little in ASHRAE but in NC they include

## Slide 50
CO2 Sen

## Slide 51: HVAC Mandatory Requirements (Cont’d)
C403.2.7 Energy Recovery
NC Threshold still > 5000 CFM and > 70% OA
Notes: This didn’t change – although it got a lot stricter in the international code the ad hoc committee declined to follow suit.

## Slide 52: C403.2.9 Ductwork Insulation (Mandatory)
R-8
R-6 (new)
R-5 (old)
NR
Notes: Only change here is R5 to R6 in unconditioned interior spaces.
In the space there is no insulation requirement for energy purposes, though it is often insulated for condensation purposes.

## Slide 53: C403.3 Economizer Requirements (Prescriptive)
Prescriptive Requirements for Economizers are Expanded
NC Maintains 65,000 btuh or less Economizer Exemption
Efficiency Exemption now for zones 3A and 4A (finally makes sense)
27%
42%
Actuator
Notes: More “this is how it is to work” language
Exempt if 27% more efficient in zone 3A; 42% more efficient in zone 4A.
Was 3B and 4B had efficiency exemptions which didn’t make sense for the dryer climates to have exemptions and not the moister climates.
Basically when they implemented our economizer requirement in 2012 they messed up by leaving out an exemption.

## Slide 54: VAV Systems (Prescriptive)
C403.4.4 Reduce Primary Airflow before reheating to one of the following:
30% of max supply to the zone.
300 CFM or less where the max flow rate is less than 10% of the total system flow rate.
Min ventilation requirements of chpt 4 of the IMC.
Any higher rate that can be demonstrated to reduce overall system annual energy use by offsetting reheat losses through a reduction in outdoor air intake for the system.
The airflow rate required to comply with applicable codes or accreditation standards, such as pressure relationships or minimum air changes.
New
New
Notes: Continuing through the highlights that are the prescriptive requirements:
We still have multizone systems are required to be VAV and the reheat has several limitations and a number of exceptions.
The problem is most jobs don’t meet the exceptions and nobody thinks they can heat adequately at 30% of primary airflow. And they figure well it’s heating mode I’m concerned about and I’m allowed to heat air – so they try and fudge around this requirement by putting the words ‘heating airflow’ in the schedule.
But that effectively makes this section meaningless and it’s intended to be complied with, not skirted.
One of the exceptions talks about controls that prevent reheating of previously cooled (or economized) air. So I think there is a way around this if you add in the logic that the min flows are not exceeded if the cooling coil is closed and the economizer is not active.
I never see this.

## Slide 55: VAV Systems (Prescriptive)
C403.4.4 Exceptions:
Zones where special pressure relationships make VAV systems impractical.
Zones where not less than 75% of the reheating is from site recovered or site solar energy source.
Zones where special humidity levels are required for process needs.
Zones with a peak supply flow of 300 CFM or less.
Zones where reheat volume is not greater than ventilation requirement of chapter 4 of the IMC.
Zones or supply air systems with controls capable of operating in sequence the supply of heating and cooling to the zones and which are capable of preventing reheating air that has been previously cooled either mechanically or through the use of an economizer.
Notes: Continuing through the highlights that are the prescriptive requirements:
We still have multizone systems are required to be VAV and the reheat has several limitations and a number of exceptions.
The problem is most jobs don’t meet the exceptions and nobody thinks they can heat adequately at 30% of primary airflow. And they figure well it’s heating mode I’m concerned about and I’m allowed to heat air – so they try and fudge around this requirement by putting the words ‘heating airflow’ in the schedule.
But that effectively makes this section meaningless and it’s intended to be complied with, not skirted.
One of the exceptions talks about controls that prevent reheating of previously cooled (or economized) air. So I think there is a way around this if you add in the logic that the min flows are not exceeded if the cooling coil is closed and the economizer is not active.
I never see this.

## Slide 56: VAV Systems (Prescriptive)
C403.4.4.6 VAV System ventilation optimization Control. ICC requirement not adopted in NC.
However, demand controlled ventilation still required on many VAV systems (>3000 CFM of OA)
Outside air at air handler based on space with highest outdoor air percentage. Each space outdoor air requirement changes with occupancy. Constantly recalculating total OA requirement.
Notes: Continuing through the highlights that are the prescriptive requirements:
We still have multizone systems are required to be VAV and the reheat has several limitations and a number of exceptions.
The problem is most jobs don’t meet the exceptions and nobody thinks they can heat adequately at 30% of primary airflow. And they figure well it’s heating mode I’m concerned about and I’m allowed to heat air – so they try and fudge around this requirement by putting the words ‘heating airflow’ in the schedule.
But that effectively makes this section meaningless and it’s intended to be complied with, not skirted.
One of the exceptions talks about controls that prevent reheating of previously cooled (or economized) air. So I think there is a way around this if you add in the logic that the min flows are not exceeded if the cooling coil is closed and the economizer is not active.
I never see this.

## Slide 57: C403.4.5 Condenser Heat Recovery for Service Water Heating (Prescriptive)
> 400 tons and 24 hour HW need
Notes: This is only applicable to large institutions with about 500 tons cooling and 1 million btuh service water load and 24 hour operation. But heat recovery is something to keep in mind on any project with large equipment.

## Slide 58: Electrical Changes
C405.2 Interior Lighting Controls:
  Now apply to more spaces including:
    Copy/Print Rooms
    Lounges
    Restrooms
    Janitorial Closets
    Mech/Elec Rooms
    Warehouses
Mandatory

## Slide 59: Electrical Changes
C405.4 Interior Lighting Power Allowances (watts/sq ft)
  Decreased for both Building Area Method and Space by Space Method in accordance with ASHRAE
Prescriptive

## Slide 60: New in Electrical
C405.6 Electric Metering (Mandatory)
  Dwellings in R-2 require separate electric meters
C405.7 Electrical Transformers and Motors (Mandatory)
  New Efficiency requirements
C405.9 Vertical/Horizontal Transportation Equipment (prescriptive)
  Lighting Control and power density requirements

## Slide 61: Commissioning
Buildings > 10,000 sq.ft.
Mechanical Systems
Service Water Heating
Power & Lighting Systems
New to NC
C408.1 Prior to a Certificate of Occupancy, a registered design professional shall provide a statement of system commissioning.
New
Notes: Now code required for buildings > 10,000 sf.
Our commissioning practices for the most part already have all this covered. But I’m not sure we include power and lighting systems.

## Slide 62: Lighting System Functional Testing
C408.3 Lighting Control Systems calibrated, adjusted, programmed per Construction Documents and Manufacturer Instructions.
  Occupant Sensor Controls
  Time Switch Controls
  Daylighting Controls
  O&M Manual for Lighting Controls

## Slide 63: Existing Buildings
Repairs
Alterations
Additions
Don’t Make Less Conforming
New Code w/Exceptions
New Work New Code
Air Barriers not required for new roofs.
Replace 50% of Luminaires if don’t increase lighting power.
AHU’s not req’d to comply with fan HP limitations.
Economizers not req’d where mod’s to roof, floor, walls needed.
Notes: There is a section on existing buildings added.

## Slide 64
Category: The 2018 NCECC
This Construction project is NOT subject to the Energy Code material of this presentation.
What is a …
New Heated Only
S-2 Repair Garage
New R-2 Residence Hall 3 stories
Conversion of Unconditioned warehouse to office space

## Slide 65
R-2 Residence Halls 3 stories or less are subject to the Residential Code.
Coming Soon: F, U, S Occupancies to be exempt (SB-131,
SL 2017-10)

## Slide 66
The End
For Questions,
Tom Galdi, PE
E-mail: tom.galdi@doa.nc.gov